Daikin North America LLC

HVAC Guide Specifications

Multiple Evaporator, Direct Expansion (DX), Air-Cooled, Variable Capacity, Split System

Section 15700 – Mechanical HVAC

Size Range:

1.5 to 4 Tons Nominal

Daikin Model Number:

FCA INDOOR UNIT – ROUND FLOW SENSING CEILING CASSETTE UNIT

FBA INDOOR UNIT – CONCEALED CEILING DUCTED UNIT (High. Static)

FTA INDOOR UNIT – MULTI-POSITION AIR HANDLING UNIT

Part 1 – GENERAL

SKYAIR AIR CONDITIONING

SPECIFICATION – Air Conditioning Only or Heat Pump Indoor Units

  - QUALITY ASSURANCE

- The units shall be tested by a Nationally Recognized Testing Laboratory (NRTL), in accordance with ANSI/UL 60335-2-40 – Heating and Cooling Equipment and bear the Listed Mark.

- All wiring shall be in accordance with the National Electric Code (NEC)/Canadian Electrical Code (CEC).

- The system will be produced in an ISO 9001 and ISO 14001 facility, which are standards set by the International Standard Organization (ISO).  The system shall be factory tested for safety and function.

- The outdoor unit will be factory charged with R32.

  - DELIVERY, STORAGE AND HANDLING

- Unit shall be stored and handled according to the manufacturer’s     recommendations.

Part 2 – WARRANTY

STANDARD LIMITED WARRANTY

Daikin North America LLC warrants original owner of the non-residential building, multifamily residence or residence in which the Daikin products are installed that under normal use and maintenance for comfort cooling and conditioning applications such products (the “Products”) will be free from defects in material and workmanship. This warranty applies to compressor and all parts and is limited in duration to ten (10) years starting from the ‘’installation date’’ which is one of the two dates below:

- The installation date is the date that the unit is originally commissioned, but no later than 18 months after the manufacture date noted on the unit’s rating plate.

- If the date the unit is originally commissioned cannot be verified, the installation date is three months after the manufacture date.

Complete warranty details available from your local Daikin representative or at www.daikincomfort.com –

Part 3 – PERFORMANCE

3.01	DESIGN BASIS

The HVAC equipment basis of design is Daikin.  All bidders shall furnish the minimum system standards as defined by the base bid model numbers, model families or as otherwise specified herein (see Key General Specifications Alternate Supplier Checklist).  In any event the contractor shall be responsible for all specified items and intents of this document without further compensation.

Part 4 – PRODUCTS

  - FCA – ROUND FLOW SENSING CEILING CASSETTE UNIT

- General:  Daikin indoor unit model FCA shall be a round flow ceiling cassette fan coil unit, operable with R32 refrigerant, equipped with an electronic expansion valve, refrigerant leak sensor, direct drive DC (ECM) type fan, for installation into the ceiling cavity equipped with an air panel grill.  It shall be available in capacities from 18,000 Btu/h to 48,000 Btu/h.  Model numbers are FCA18AAVJU, FCA24AAVJU, FCA30AAVJU, FXC36AAVJU, FCA42AAVJU, FCA48AAVJU to be connected to outdoor unit model RZA SkyAir Heat Pump.  It shall be a round flow air distribution type, fresh white, impact resistant decoration panel, or optional self-cleaning filter panel.  The supply air is distributed via four individually motorized louvers.  To save energy and optimize occupancy comfort, the indoor unit shall be equipped with built in occupancy sensor and surface temperature sensor. Computerized PID control shall be used to control superheat to deliver a comfortable room temperature condition.   The unit shall be equipped with a programmed drying mechanism that dehumidifies while limiting changes in room temperature when used with Daikin remote control BRC1NRV71.  The indoor units sound pressure shall range from 38 dB(A) to 47 dB(A) at High speed measured at 5 feet below the unit.

- Performance: Each unit’s performance is based on nominal operating conditions:

| Model Number | Cooling (Indoor 80°F DB / 67°F WB, Outdoor 95°F DB, 25 ft pipe length) | Heating (Indoor 70°F DB Outdoor 47F / 43F, 25 ft pipe length) |
| --- | --- | --- |
| FCA18AAVJU | 18,000 | 20,000 |
| FCA24AAVJU | 24,000 | 27,000 |
| FCA30AAVJU | 30,000 | 34,000 |
| FCA36AAVJU | 36,000 | 40,000 |
| FCA42AAVJU | 42,000 | 47,000 |
| FCA48AAVJU | 48,000 | 54,000 |

- Indoor Unit:

- The Daikin indoor unit FCA shall be completely factory assembled and tested.  Included in the unit is factory wiring, piping, electronic proportional expansion valve, control circuit board, fan motor thermal protector, flare connections, condensate drain pan, condensate drain pump, condensate safety shutoff and alarm, self-diagnostics, auto-restart function, 3-minute fused time delay, and test run switch.

- The indoor unit shall have a factory installed refrigerant leak sensor built in.  If a leak is detected, the unit shall go into circulation mode and provide full airflow.  The unit shall have signal output in event of leak to connect to external ventilation, damper, alarm etc.

- Indoor unit and refrigerant pipes will be charged with dehydrated air prior to shipment from the factory.

- Both refrigerant lines shall be insulated from the outdoor unit.

- The round flow supply air flow can be field modified to 18 different airflow patterns to accommodate various installation configurations including corner installations.

- Return air shall be through the concentric panel, which includes a resin net, mold resistant, antibacterial filter.

- The indoor units shall be equipped with a condensate pan with antibacterial treatment and condensate pump. The condensate pump provides up to 33-1/2” of lift from bottom of unit to top of drain piping and has a built in safety shutoff and alarm.

- The indoor units shall be equipped with a return air thermistor.

- The indoor unit will be separately powered with 208~230V/1-phase/60Hz.

- The voltage range will be 253 volts maximum and 187 volts minimum.

- To save energy and optimize occupancy comfort, the indoor unit shall be equipped with built in occupancy sensor and surface temperature sensor.

- Supplied air shall be directed automatically by four individually controlled louvers.

- Unit Cabinet:

- The cabinet shall be space saving and shall be located into the ceiling.

- Four auto-adjusted louvers shall be available to choose, which include standard, draft prevention and ceiling stain prevention.

- The airflow of the unit shall have the ability to shut down outlets with multiple patterns allowing for simpler installation in irregular spaces.

- Fresh air intake shall be possible by way of Daikin’s optional fresh air intake kit.

- A branch duct knockout shall exist for branch ducting of supply air.

- The cabinet shall be constructed with sound absorbing foamed polystyrene and polyethylene insulation.

- Optional high efficiency air filters are available for each model unit.

- Fan:

- The fan shall be direct-drive DC (ECM) type fan, statically and dynamically balanced impeller with three fan speeds available.

- The fan motor shall operate on 208/230 volts, 1 phase, 60 hertz with a motor output range from 0.08 to 0.16 HP.

- The airflow rate shall be available in three manual settings.

- The DC fan shall be able to automatically adjust the fan speed in 5 speeds based on the space load.

- The fan motor shall be equipped as standard with adjustable external static pressure (ESP) settings to allow operation with the high efficiency air filter options.

- The fan motor shall be thermally protected.

- Filter:

- The return air shall be filtered by means of a washable long-life filter with mildew proof resin and antibacterial treatment.

- Optional high efficiency disposable air filters shall be available.

- Optional Self-Cleaning Filter Panel, which performs automatic filter cleaning up to once a day, with dust collection box that indicates when to be emptied.

- Coil:

- Coils shall be of the direct expansion type constructed from copper tubes expanded into aluminum fins to form a mechanical bond.

- The coil shall be of a waffle louver fin and high heat exchange, rifled bore tube design to ensure highly efficient performance.

- The coil shall be a 2, or 3-row cross fin copper evaporator coil with up to 21 FPI design completely factory tested.

- The refrigerant connections shall be flare connections and the condensate will be 1 -1/4 inch outside diameter PVC.

- A condensate pan with antibacterial treatment shall be located under the coil.

- A thermistor will be located on the liquid and gas line.

- Electrical:

- A separate power supply will be required of 208/230 volts, 1 phase, 60 hertz. The acceptable voltage range shall be 187 to 253 volts.

- Transmission (control) wiring between the indoor and outdoor unit shall be a maximum of 3,280 feet.

- Transmission (control) wiring between the indoor unit and remote controller shall be a maximum distance of 1,640 feet.

- Control:

- The unit shall have controls provided by Daikin to perform input functions necessary to operate the system.

- The unit shall be compatible with interfacing with a BMS system via optional LonWorks or BACnet gateways.

- The unit shall be compatible with a Daikin Intelligent Touch Manager advanced multi-zone controller.

- For the Sensing functions and the optional Self-Cleaning Filter functions, Remote controller BRC1NRV71 shall be used. Consult with Daikin prior to applying controls.

- Optional Accessories Available:

- A high efficiency disposable air filter kit

- Air intake kit

- Self-Cleaning Filter Panel, which performs automatic filter cleaning up to once a day, with dust collection box that indicates when to be emptied.

- Remote “in-room” sensor kit (KRCS01-6B).

    - The Daikin wall mounted, hard wired remote sensor kit is recommended for when a NAV controller is not used or when the NAV controller is not located in the space that is being controlled. The sensor for detecting the temperature can be placed away from the indoor unit (branch wiring is included in the kit).

4.08	FBA - CONCEALED CEILING DUCTED UNIT (High Static)

- General Requirements:

  - All indoor/evaporator units shall be factory assembled and tested DX-fan coil units, operable with refrigerant R32.

  - All units shall be completely factory assembled and tested, and shall be charged with dehydrated air prior to shipment from the factory.

  - All units shall be equipped with an electronic expansion valve controlled using a PID loop to automatically adjust the refrigerant flow rate through the unit.

  - All units shall be equipped with a programmed drying   operation that dehumidifies while limiting changes in room temperature when used with Daikin remote controllers BRC1NRV71.

  - All units shall feature self-diagnostics, auto-restart functionality, 3-minute fused time delay, and a test run switch.

  - All refrigerant piping, both liquid and suction, shall be fully insulated from the outdoor unit.

- Performance: Each unit’s performance is based on nominal operating conditions:

| Model Number | Cooling (Btu/h) (Indoor 80°FDB / 67°FWB, Outdoor 95°FDB, 25 ft pipe length) | Heating (Btu/h) (Indoor 70°FDB, Outdoor 47°FDB / 43°FWB, 25 ft pipe length) |
| --- | --- | --- |
| FBA18AAVJU | 18,000 | 20,000 |
| FBA24AAVJU | 24,000 | 27,000 |
| FBA30AAVJU | 30,000 | 34,000 |
| FBA36AAVJU | 36,000 | 40,000 |
| FBA42AAVJU | 40,500 | 47,000 |
| FBA48AAVJU | 48,000 | 54,000 |

- Indoor Unit:

- The Daikin indoor unit FBA shall be completely factory assembled and tested.  Included in the unit is factory wiring, piping, electronic proportional expansion valve, control circuit board, fan motor thermal protector, flare connections, condensate drain pan, condensate drain pump, condensate safety shutoff and alarm, self-diagnostics, auto-restart function, 3-minute fused time delay, and test run switch. The unit shall be equipment with automatically adjusting external static pressure logic that is selectable during commissioning. This adjusts the airflow based on the installed external static pressure.

- The indoor unit shall have a factory installed refrigerant leak sensor built in.  If a leak is detected, the unit shall go into circulation mode and provide full airflow.  The unit shall have signal output in event of leak to connect to external ventilation, damper, alarm etc.

- Indoor unit and refrigerant pipes will be charged with dehydrated air prior to shipment from the factory.

- Both refrigerant lines shall be insulated from the outdoor unit.

- The indoor units shall be equipped with a return air thermistor.

- The indoor unit will be separately powered with 208~230V/1-phase/60Hz.

- The voltage range will be 253 volts maximum and 187 volts minimum.

- Unit Cabinet:

  - The unit cabinet shall be constructed of heavy gauge galvanized steel.

  - The unit shall be internally insulated and shall be capable of installation in indoor environments up to 80% relative humidity without requiring additional field installed insulation.

  - The unit shall ship from the factory in a rear-return configuration and shall be field-convertible to a bottom-return configuration.

  - The unit shall be equipped with a return air thermistor.

  - The cabinet shall be constructed with sound absorbing foamed fiber-less closed cell polystyrene and polyethylene insulation.

- Fan:

  - The fan shall be a direct-drive, brushless DC fan motor with (3) user-selectable fan speeds (H, M, L).

  - The unit shall be equipment with automatically adjusting external static pressure logic selectable during commissioning.

  - The unit shall be equipped with internal controls to allow the fan to automatically select the operating fan curve to deliver nominal airflow CFM (within +/- 10%) when the connect ductwork has been designed with a total external static within the range of the FBA.  This setting shall be accessible as a setting to be used during startup and commissioning of the system

  - The fan motor shall be capable of Auto fan speed control when the unit is connected to the BRC1NRV71 Navigation Remote Control.  The Auto fan speed control shall automatically adjust the unit’s fan speed in response to the difference between the indoor unit’s current set point and the current room temperature measurement.  The Auto fan speed control shall utilize (5) fan speeds.

  - The fan motor shall be internally isolated using rubber grommets to reduce transmission of vibrations to the unit.

- The airflow rate shall be available in three settings.

- The fan motor shall be thermally protected.

- Fan motor external static pressure range for nominal airflow:

| Model Number | Fan ESP (in. w.g.) |
| --- | --- |
| FBA18AAVJU | 0.20 – 0.80 |
| FBA24AAVJU | 0.20 – 0.80 |
| FBA30AAVJU | 0.20 – 0.80 |
| FBA36AAVJU | 0.20 – 0.80 |
| FBA42AAVJU | 0.20 – 0.80 |
| FBA48AAVJU | 0.20 – 0.80 |

- Fan Blade

  - The fan blade shall be constructed of lightweight polymer.

  - The fan blade shall be statically and dynamically balanced to minimize vibration.

- Coil:

  - Coils shall be of the direct expansion type, constructed from copper tubes expanded into aluminum fins to form a mechanical bond.

  - The coil shall be of a waffle louver fin and high heat exchange, rifled bore tube design to ensure highly efficient performance.

  - The coil shall be 2 or 3 row cross fin copper evaporator coil with 18 fpi design, completely factory tested.

  - The refrigerant connections shall be flare connections.

  - Factory mounted thermistors shall be installed on the liquid and gas lines.

- Condensate Drainage

  - The unit shall be equipped with a condensate drain pan under the coil.

  - The condensate drain outlet shall be of PVC construction and VP25 (1” ID, 1-1/4” OD).

  - The unit shall be equipped with a factory-integral condensate pump capable of 25-5/16” lift from the condensate drain outlet.  The condensate pump shall be equipped with a float switch to automatically stop unit operation and provide a system error code in the event drain pan water level rises too high.

- Electrical:

  - Provide a separate power supply connection of 208/230V, 1 phase, 60 hertz.  The allowable voltage range shall be 187 to 253 volts.

  - Refer to the engineering data book for all other electrical data including MCA, MOCP, and FLA values.

  - The transmission (control) wiring distance between the indoor unit and outdoor unit shall be a maximum of 3,280 feet.

  - The transmission (control) wiring between the indoor unit and the remote controller shall be a maximum distance of 1,640 feet.

- Control:

  - The unit shall be controlled with a Daikin remote controller to perform input functions necessary to operate the system.

  - The unit shall be compatible with interfacing with a building management system (BMS) via optional BACnet or LonWorks gateways.

  - The unit shall be compatible with a Daikin Intelligent Touch Manager advanced multi-zone controller.

- Optional Accessories Available:

  - BRC1NRV71 Navigation Remote Controller (wired)

  - KRCS01-6B Remote Sensor

4.03	FTA – MULTI-POSITION AIR HANDLING UNIT

- General:  Daikin indoor unit FTA shall be a floor mounted vertical, horizontal left, horizontal right, or downflow air handling unit, operable with refrigerant R32, equipped with an electronic expansion valve and direct-drive ECM type fan with constant CFM programming, for installation within a conditioned space.  When installed in a vertical configuration it shall have top discharge air and bottom return air.  When installed in a horizontal right or horizontal left configuration, it shall have a horizontal discharge air and horizontal return air.  When installed in a downflow configuration it shall have bottom discharge and top return air.  This compact design with pre-painted heavy-gauge steel casing shall be available in capacities from 18,000 Btu/h to 48,000 Btu/h.  Model numbers are FTA18AAVJUA, FTA24AAVJUA, FTA30AAVJUA, FTA36AAVJUA, FTA42AAVJUA, and FTA48AAVJUA to be connected to outdoor unit model RZA SkyAir Heat Pump.  The FTA series may also be specified to utilize a factory integral disconnect switch.  Model numbers including the factory disconnect are FTA18AAVJUD, FTA24AAVJUD, FTA30AAVJUD, FTA36AAVJUD, FTA42AAVJUD, and FTA48AAVJUD.   A KRCS01-6B remote temperature sensor kit shall be required for all FTA indoor units not utilizing the thermistor in the Daikin remote controller BRC1NRV71.  Computerized PID control shall be used to control superheat to deliver a comfortable room temperature condition.  The unit shall be equipped with a programmed drying mechanism that dehumidifies while limiting changes in room temperature when used with Daikin remote control BRC1NRV71.

- Performance: Each unit’s performance is based on nominal operating conditions: See AHRI for Ratings.

| Model Number | Cooling (Indoor 80°F DB / 67°F WB, Outdoor 95°F DB, 25 ft pipe length) | Heating (Indoor 70°F DB Outdoor 47F / 43F, 25 ft pipe length) |
| --- | --- | --- |
| FTA18AAVJUA(D) | 17,200 | 21,000 |
| FTA24AAVJUA(D) | 24,000 | 27,000 |
| FTA30AAVJUA(D) | 29,400 | 35,000 |
| FTA36AAVJUA(D) | 35,000 | 40,500 |
| FTA42AAVJUA(D) | 40,500 | 48,000 |
| FTA48AAVJUA(D) | 47,000 | 55,000 |

- Indoor Unit:

- The Daikin indoor unit FTA_AA components shall be completely factory assembled and tested.  Included in the unit is factory wiring, piping, electronic proportional expansion valve, control circuit board, fan motor thermal protector, brazed connections, self-diagnostics, auto-restart function, 3-minute fused time delay, and test run switch.

- Indoor unit and refrigerant pipes will be charged with dehydrated air prior to shipment from the factory.

- Both refrigerant lines shall be insulated from the outdoor unit.

- Return air shall be through an optional or field supplied filter.

- Condensate draining shall be made via gravity or external condensate pump.

- The indoor unit will be separately powered with 208~230V/1-phase/60Hz.

- The voltage range will be 253 volts maximum and 187 volts minimum.

- Unit Cabinet:

- The cabinet shall be constructed with sound absorbing, foil-faced insulation to control air leakage.

- Select an installation location with adequate structural support, space for service access and clearance for air return and supply duct connections.

- A field supplied secondary drain pan shall be installed where required by national, state, or local code.

- Fan:

- The fan shall be a direct-drive Sirocco type fan, statically and dynamically balanced impeller with high and low fan speeds available.

- The fan motor shall operate on 208/230 volts, 1 phase, 60 hertz with a motor output range 0.2 to 1.0. HP.

- The airflow rate shall be available in high setting.

- The fan motor shall be thermally protected.

- Fan motor external static pressure for nominal airflow:

| Model Number | Fan ESP (in. WG) |
| --- | --- |
| FTA18AAVJUA(D) | Up to 0.9 |
| FTA24AAVJUA(D) | Up to 0.9 |
| FTA30AAVJUA(D) | Up to 0.9 |
| FTA36AAVJUA(D) | Up to 0.9 |
| FTA42AAVJUA(D) | Up to 0.9 |
| FTA48AAVJUA(D) | Up to 0.9 |

- Filter:

- The return air shall be filtered by means of an optional or field supplied filter.

- Coil:

- Coils shall be of the direct expansion type constructed from aluminum tubes expanded into aluminum fins to form a mechanical bond.

- The coil shall be of a waffle louver fin and high heat exchange, rifled bore tube design to ensure highly efficient performance.

- The coils shall be a 2- to 4-row cross fin copper evaporator coil with 14 to 16 fpi design completely factory tested.

- The refrigerant connections shall be brazed connections and the condensate will be 3/4 inch outside diameter PVC.

- A thermistor will be located on the liquid and gas line.

- Electrical:

- A separate power supply will be required of 208/230 volts, 1 phase, 60 hertz. The acceptable voltage range shall be 187 to 253 volts.

- Transmission (control) wiring between the indoor and outdoor unit shall be a maximum of 3,280 feet.

- Transmission (control) wiring between the indoor unit and remote controller shall be a maximum distance of 1,640 feet.

- Control:

- The unit shall have controls provided by Daikin to perform input functions necessary to operate the system.

- The unit shall be compatible with interfacing with a BMS system via optional LonWorks or BACnet gateways.

- The unit shall be compatible with a Daikin Intelligent Touch Manager advanced multi-zone controller.

- Optional Accessories Available:

  - Field installed 3-25kW electric heaters (HKTS-03, HKTS-05, HKTS-06, HKTS-08, HKTS-10, HKTS-15, HKTS-19).

  - Remote sensor KRCS01-6B

  - BRC1NRV71 wireless controller.

Part 5 - HVAC EQUIPMENT ALTERNATE (GENERAL INFORMATION)

5.01	The alternate equipment supplier shall provide to the bidding mechanical contractor a complete equipment data package.  This package shall include, but is not limited to, equipment capacities at the design condition, power requirements, indoor units CFM/static pressures, fan curves, installation requirements, and physical dimensions.  Nominal performance data is not acceptable.

The mechanical contractor shall request and receive the equipment data package 15 days prior to bid date and submit this package with the alternate bid.

The mechanical contractor shall list the equipment supplier and submit the required data package with the bid detailing a complete comparison of the proposed alternate equipment to the specified equipment and the associated cost reduction of the alternate equipment. The contractor bids an alternate manufacturer with full knowledge that that manufactures product may not be acceptable or approved.

5.02	The alternate equipment supplier shall furnish a complete drawing package to the mechanical contractor 15 days prior to bid day for bidding and installation. The drawing format shall be .dxf or equivalent, on 30"x42" sheets.  The HVAC and electrical series design documents will be made available in electronic format for use by the equipment supplier in preparing their drawings. The alternate equipment supplier shall prepare the following drawings:

XXX	HVAC Floor Plan
XXX	HVAC Refrigerant Piping Plan

XXX	HVAC Refrigerant Piping/Controls Details

XXX	HVAC Details

XXX	HVAC Schedules

The alternate equipment supplier shall draft all piping circuits, components, overall building control schematic, detailed control wiring diagrams, system details and schedules for their system.  The drawings shall convey all requirements to successfully install the alternate equipment suppliers system.

Provide (2) drawing package sets plotted on 20 lb. vellum.  Provide (1) drawing package in electronic format (.dxf files) on CD.

The submitted documents shall be complete system designs and show no less information than the HVAC equipment/controls contract bid documents.

5.03  	The equipment supplier shall submit as part of the equipment data package outdoor unit data sheets.  Data sheets to include the following:

Capacities at project design conditions: Cooling

Cooling (Btu/h)

Cooling Input Power

(kW)

Capacities at project design conditions: Heating

Heating (Btu/h)

Heating Input Power

(kW)

The submitted capacity and efficiency performance must meet or exceed the listed performance on the schedule at the designed outdoor ambient, and indoor space temperature conditions including de-rate factors for defrost and refrigerant piping lengths.

Operating Temperature Range:

Cooling

Heating

Power Supply:

Maximum Circuit Amps (MCA)

Maximum Overcurrent Protection Amps (MOP)

Maximum Starting Current (MSC)

Outdoor Fan Motor

Refrigerant:

Refrigerant Type/Charge

Control

Unit Data:

Max. Number of Indoor Units

Sound Pressure Level at 3ft. (dBA)

Weight (lbs)

Dimensions

5.04	The equipment supplier shall guarantee the performance of their system and all published data submitted.  Performance shall be based on the design criteria below.

Room Temperature (Cooling):  _________________________________

Room Temperature (Heating):  _________________________________

Ambient Temperature (Summer):  _______________________________

Ambient Temperature (Winter):  ________________________________

Defrost De-rate Factor:  _______________________________________

Refrigerant Piping Loss in cooling (correction factor):  _______________

Refrigerant Piping Loss in heating (correction factor):  _______________

5.05	The alternate equipment supplier shall submit with bid, indoor unit data sheets.  Data sheets to include the following:

Capacities:

Cooling (Btu/h)

Heating (Btu/h)

Air Flow (CFM)

External Static Pressure (ESP)

Electrical Data (MCA, MOP, MSC)

Weight (lbs)

Dimensions